## Summary - Final
Principle Architect
MEP Consultant
Contractor
TITLE :
TAGORE CASUALTY BLOCK THIRD FLOOR
S.NO | Scope | BOQ Approved
|  | BOQ Supply Value | BOQ Erection Value | Total BOQ Value | GST | Total (Including GST)
1 | Low Side Electrical | 13949963 | 2624610 | 16574573 | 2983423.14 | 19557996.14
2 | FAS - Fire Alarm System | 429720 | 166390 | 596110 | 107299.8 | 703409.8
3 | CCTV & Networking | 563080 | 137570 | 700650 | 126117 | 826767
Total Boq Value Approved ( Including GST) | [5 empty] | 21088172.94

## Low Side Electrical
Architect
MEP Consultant
Contractor
TITLE :
Sl.No | DESCRIPTION | Qty | Unit | Rate |  | Amount
|  |  |  | Supply | Erection | Supply | Erection
Part – A - PANELS, CABLES & TERMINATION
Section I - PANELS
I | LT PANELS (PANEL VENDOR SHALL BE CPRI CERTIFIED FOR SHORT CIRCUIT and IP TEST, the test should have been carried within last 5 years citing the updation in norms)
Supply , Installation , Testing & commissioning of all low tension panels indicated in this section shall be of similar construction specially fabricated, compartmentalised independent, floor / Wall mounting type made out of 14 SWG for Support Membrane, 10 SWG for Gland Plate /14 SWG for Rest of Panel including Door CRCA sheet, EPOXY powder coated after full chemical pretreatment and Eleven tank process.
Notes :
a) All busbars shall be of Aluminium unless otherwise specified and provided with colour coded PVC sleeves.
b) Adequate depth/ distances between gland plates and lugs connections shall be provided for cable connections.
d) Construction of all panels shall be IP 52 with ventilating louvers and fine brass wire mesh where required by design.
e) Incomer shall be in separate compartment.
f) Interphase barriers shall be provided.
g) Indicating lamps shall be of cluster LED type.
h) All meters shall be of digital type without RS 485 port unless specified
i) Cable connection can be from top or bottom depending on the location of the panels. Contractor shall check before preparing G.A. drawings.
j) All panels shall include terminations suitable for the cable sizes indicated in the single line diagram.
k) All Current Transformer shall be tape wound.
l) All MCCBs shall be Adjustable OL & fixed SC
m) All ACBs & MCCBs Breaking capacity shall be of Icu = Ics 100%
n) Finish - Rittal Grey RAL - 7035 (Epoxy power coating, Texture finish)
o)Al MCCB up to 200A Thermal magnetic based, 250A and above rating MCCB's are micro processor based LSING protection
p) Main LT Panel all EDO ACB Incomers shut trip coil as 230 V AC
q) Rs.485 Port Provided Only Main LT Panel Incomer Meters..
r) All MCCB shall have range adjustable from 40% to 100%
s) All control cable shall be 1.5Sqmm only
t) Aluminium Busbar shall be used from 63A and above, below 63A it shall be Uninyvyn Copper braided Cables only to be used. Flexible PVC cables should not be used
u) All Aluminium Bus Bar Shall be Electrolytic Type only and 0.7A/Sq.mm shall be taken for sizing
v) AL bus bar size of Phase and Neutral shall be the same for R, Y, B and Neutral, Earth Bus shall be 50% of the Main Bus Rating
w) All the Base Plinth shall be made with ISMC only and shall be Black Matt Epoxy Powder Coated with 11 tank process only. Spray painting or hand painting with black is not permitted
1 | MAIN L.T.PANEL | 1 | Nos | 1185155 | 35400 | 1185155 | 35400
INCOMER 1
1No. - 630A, 50kA, 4 pole MCCB with micro processor O/C,S/C, E/F releases shunt trip and under voltage release
1 set-Indicating lamps RYB with control MCB
1 set - ON,OFF, TRIP indication lamp
1 No- Load Manager / Demand Controller' Conzerv / Elmeasure / LK make
1 No - MFM with Harmonics data Model similar to EM6400 Conzerv / Elmeasure / LK make
1 No - Surge Protective Devices with 63A MPCB (Type-1)
1set - Reverse power relay (L&T) with 400/5A, 15VA , Class 5P10 CT
1 No - Phase Failure Relay
3 Nos.- Current Transformers of ratio 400 / 5A, 15 VA burden & accuracy Class 1 for metering
1 No.- Current Transformer of ratio 400/ 5A , 15VA , Class 1 for connection to APFC panel
INCOMER - 2
1 No. - 630A, 50kA, 4 pole MCCB with micro processor O/C,S/C, E/F releases shunt trip and under voltage release
1set -indicating lamps RYB with control MCB
1set - ON,OFF, TRIP indication lamp
1Nos - Phase Failure Relay
1 No- Load Manager / Demand Controller' Conzerv / Elmeasure / LK make
1set - Reverse power relay (L&T) with 400/5A, 15VA , Class 5P10 CT, Class 1.0
1 Nos – 63A 4P MPCB
1 No - Surge Protective Devices with 63A MPCB (Type-1)
3 Nos. - Current Transformers of ratio 400/5A, 15 VA, CL1.0.for metering
SOLAR INCOMER
1 NoS. - 315A, 36kA, 4 pole MCCB, T/M, UV and Shunt Coil
Outgoings :
Provide ON, OFF, TRIP Indication lamp
Provide KWH meter (Conzerv make /Equivalent) with necessary CTs and indication lamp.
Bus section
1 Nos – 250A FP MCCB 36KA. AC ODU PANEL
2 Nos – 160A FP MCCB 36KA. APFC, Spare
5 Nos - 125A FP MCCB 36KA. (OT AC, OT PDB, LAB PDB, Blood Bank UPS, Spare)
7Nos - 100A FP MCCB 25KA. (ACDB, Blook Bank ACDB, Blood Bank PDB, Blood Bank VTPN, OT UPS, Spare)
3 Nos - 80A FP MCCB 25KA. (Semi Private Rooms PDB, Wards UPS, Spare)
Busbars :
630A TPN Aluminium busbars (0.7A/Sq.mm) - 100mm x 10mm for R, Y, B, N
50x10 Aluminium Earth Bus
25x10 Aluminium Earth Bus
2 | 50 KVAR APFC PANEL With Detuned Harmonic filters and Contactor switching modules comprising the following: (12 Step Controller) | 1 | Nos | 597180 | 17500 | 597180 | 17500
1 No – 160A TP+N Microprocessor Type MCCB 36KA.
1 set - Indicating lamps R, Y, B.
1 No - Digital volt meter
1 No - Digital ammeter with suitable CT
1 No - Auto/Manual sel. Switch
1 No - APFC relay (8 Stage)
Busbars :
400A TPN Aluminium busbars (0.7A/Sq.mm)
30x6 Copper Earth Bus
Outgoings:
63A TP, Thermal Magnetic Release, MCCB, 25KA - 2 nos
40A TP, Thermal Magnetic Release, MCCB, 16KA - 5 nos
32A TP, Thermal Magnetic Release, MCCB, 16KA - 4 nos
15 KVAR MPP Gas filled Heavy duty capacitor with 7 % detuned harmonic filter and Thyristor module units to be protected by 63A TP MCCB 25 KA, 1no of ON/OFF Indication /push button – 1 sets
10 KVAR MPP Gas filled Heavy duty capacitor with 7 % detuned harmonic filter and Thyristor module units to be protected by 63A TP MCCB 25 KA, 1no of ON/OFF Indication /push button – 1set
5 KVAR MPP Gas filled Heavy duty capacitor with 7 % detuned harmonic filter and Thyristor module units to be protected by 40A TP MCCB 25 KA, 1no of ON/OFF Indication /push button – 3set
2.5 KVAR MPP Gas filled Heavy duty capacitor with 7 % detuned harmonic filter and Thyristor module units to be protected by 32A TP MCCB 25 KA, 1no of ON/OFF Indication /push button – 4set
3 | Sub Isolation Panel 1
| 160A FP MCCB, 36KA, With with micro processor O/C,S/C, E/F releases & 150Sqmm Suitable Power Terminal block for Incoming and Outgoing power Termination | R0 | Nos | 60150 | 5000
4 | Lighting Panel | 1 | Nos | 316585 | 15500 | 316585 | 15500
CABLE ENTRY : BOTTOM
Supplying, erecting, connecting and commissioning of FLOOR MOUNTED with Base Channel increasing height of the panel from floor by 500mm to ensure cable entry is possible through bottom
Overall height of the panel including Base Channel shall not exceed 2000mm, also the maximum operating handle height shall not exceed 1800mm
A/C Panel with necessary foundation channels, etc.,
The Board shall be incorporated with the following:-
All MCCBs shall be of Thermal Magnetic Type with adjustable
overloads and fixed short circuits (Ics=100%Icu)
INCOMER :
125AMPS TPN MCCB 36 KA(Ics = 100% Icu) With standing Capacity …02No.
Busbars :
125A TPN Aluminium busbars (0.7A/Sq.mm)
30x6 Copper Earth Bus
OUTGOINGS :
63 AMPS TPN MCCB 25 KA(Ics = 100% Icu) withstanding Capacity ..6 Nos.
40 AMPS TPN MCCB 25 KA(Ics = 100% Icu) withstanding Capacity ..4 Nos.
5 | AC ODU Panel - OUTDOOR TYPE - Terrace (Double door with canopy for OT AC and Rooms VRF)
| CABLE ENTRY : BOTTOM | 1 | Nos | 333522 | 15500 | 333522 | 15500
Supplying, erecting, connecting and commissioning of FLOOR MOUNTED with Base Channel increasing height of the panel from floor by 500mm to ensure cable entry is possible through bottom
Overall height of the panel including Base Channel shall not exceed 2000mm, also the maximum operating handle height shall not exceed 1800mm
A/C Panel with necessary foundation channels, etc.,
The Board shall be incorporated with the following:-
All MCCBs shall be of Thermal Magnetic Type with adjustable
overloads and fixed short circuits (Ics=100%Icu)
INCOMER :
250AMPS TPN MCCB 36 KA(Ics = 100% Icu) With standing Capacity …01No. (From RM1 and RM2) connected to common Busbar with mechanical interlock
Busbars :
250A TPN Aluminium busbars (0.7A/Sq.mm)
30x6 Copper Earth Bus
OUTGOINGS :
100 AMPS TPN MCCB 25 KA(Ics = 100% Icu) withstanding Capacity ..6 Nos. (For DRF ODU and Spare)
63 AMPS TPN MCCB 25 KA(Ics = 100% Icu) withstanding Capacity ..6 Nos. for ADCB and spare
6 | GIRLS HOSTEL SUB PANEL TO BE POSITIONED IN THIRD FLOOR | 1 | Nos | 376486 | 15500 | 376486 | 15500
CABLE ENTRY : BOTTOM
Supplying, erecting, connecting and commissioning of FLOOR MOUNTED with Base Channel increasing height of the panel from floor by 500mm to ensure cable entry is possible through bottom
Overall height of the panel including Base Channel shall not exceed 2000mm, also the maximum operating handle height shall not exceed 1800mm
A/C Panel with necessary foundation channels, etc.,
The Board shall be incorporated with the following:-
All MCCBs shall be of Thermal Magnetic Type with adjustable
overloads and fixed short circuits (Ics=100%Icu)
INCOMER :
250AMPS TPN MCCB 36 KA(Ics = 100% Icu) With standing Capacity …02No.
Busbars :
250A TPN Aluminium busbars (0.7A/Sq.mm)
30x6 Copper Earth Bus
OUTGOINGS :
100 AMPS TPN MCCB 25 KA(Ics = 100% Icu) withstanding Capacity ..5 Nos.
63 AMPS TPN MCCB 25 KA(Ics = 100% Icu) withstanding Capacity ..5 Nos.
7 | LIGHTING DISTRIBUTION BOARD (Lab / Blood bank / Rooms) | 3 | Nos | 18030 | 3200 | 54090 | 9600
Supply & Erection of 3 Phase, 4 way, Phase seggregated 7 Seg., LDB Double door TPN DB , with anchor fastener ,bolt & nuts and earthing.
Incoming : 63A / 40A 4P MCB - 1 No
Outgoing : 32A DP RCBO (30mA) - 3 Nos
6A SP MCB - 12 Nos
8 | LIGHTING DISTRIBUTION BOARD (Common Area) | 1 | Nos | 17300 | 3200 | 17300 | 17300
Supply & Erection of 3 Phase, 4 way, Phase seggregated 7 Seg., LDB Double door TPN DB , with anchor fastener ,bolt & nuts and earthing.
Incoming : 40A 4P MCB - 1 No
Outgoing : 25A DP RCBO (30mA) - 3 Nos
6A SP MCB - 12 Nos
9 | LIGHTING DISTRIBUTION BOARD (MBBS Girls Hostel - Third Floor) | 1 | Nos | 17300 | 3200 | 17300 | 17300
Supply & Erection of 3 Phase, 4 way, Phase seggregated 7 Seg., LDB Double door TPN DB , with anchor fastener ,bolt & nuts and earthing.
Incoming : 40A 4P MCB - 1 No
Outgoing : 25A DP RCBO (30mA) - 3 Nos
6A SP MCB - 12 Nos
10 | EMERGENCY LIGHTING DISTRIBUTION BOARDS (wards / Labs / OT / Blood Bank) | 4 | Nos | 5580 | 1250 | 22320 | 89280
Supply & Erection of single phase 12 way SPN DB EMERGENCY LIGHTING DB lightpoint Cost should include chipping,removing debris, repacking Power plug point Cost should include chipping,removing debris, repacking with cement mortor, curing Complete Work.
Incoming : 32A DP RCBO, 30mA - 1 No
Outgoing : 6A SP MCB - 8 Nos
11 | EMERGENCY LIGHTING DISTRIBUTION BOARDS (MBBS Girls Hostel - Third Floor - dedicated inverter mentioned in Part D) | 1 | Nos | 5580 | 1250 | 5580 | 5580
Supply & Erection of single phase 12 way SPN DB EMERGENCY LIGHTING DB lightpoint Cost should include chipping,removing debris, repacking Power plug point Cost should include chipping,removing debris, repacking with cement mortor, curing Complete Work.
Incoming : 32A DP RCBO, 30mA - 1 No
Outgoing : 6A SP MCB - 8 Nos
12 | POWER DISTRIBUTION BOARDS (PDB) (OT & LAB) | 2 | Nos | 28010 | 4200 | 56020 | 8400
Supply & Erection of 3 Phase, 8 way, Phase seggregated 7 Seg., PDB Double door TPN DB , with anchor fastener ,bolt & nuts and earthing.
Incoming : 125A / 100A 4P MCB - 1 No
Outgoing : 40A DP RCCB (30mA) - 3 Nos
20A SP MCB - 12 Nos
16A SP MCB - 12 Nos
13 | POWER DISTRIBUTION BOARDS (PDB) (Blood Bank / Rooms) | 2 | Nos | 27450 | 4200 | 54900 | 8400
Supply & Erection of 3 Phase, 8 way, Phase seggregated 7 Seg., PDB Double door TPN DB , with anchor fastener ,bolt & nuts and earthing.
Incoming : 100A 4P MCB - 1 No
Outgoing : 40A DP RCCB (30mA) - 3 Nos
20A SP MCB - 12 Nos
16A SP MCB - 12 Nos
14 | POWER DISTRIBUTION BOARDS (PDB) (MBBS Girls Hostel - Third Floor) | 1 | Nos | 27450 | 4200 | 27450 | 4200
Supply & Erection of 3 Phase, 8 way, Phase seggregated 7 Seg., PDB Double door TPN DB , with anchor fastener ,bolt & nuts and earthing.
Incoming : 100A 4P MCB - 1 No
Outgoing : 40A DP RCCB (30mA) - 3 Nos
20A SP MCB - 12 Nos
16A SP MCB - 12 Nos
15 | UPS DB (Blood Bank / OT / LAB) | 3 | Nos | 28010 | 4200 | 84030 | 252090
Supply & Erection of 3 Phase, 8 way, Phase seggregated 7 Seg., Double door TPN DB , with anchor fastener ,bolt & nuts and earthing.
Incoming : 125A 4P MCB - 1 No
Outgoing : 40A DP RCCB (30mA) - 3 Nos
16A SP MCB - 24 Nos
16 | UPS DISTRIBUTION BOARDS Rooms | 1 | Nos | 5580 | 1250 | 5580 | 1250
Supply & Erection of single phase 12 way SPN DB UPS Power DB for Room Sockets towards connecting monitors Cost should include chipping,removing debris, repacking Power plug point Cost should include chipping,removing debris, repacking with cement mortor, curing Complete Work.
Incoming : 32A DP RCBO, 30mA - 1 No
Outgoing : 6A SP MCB - 8 Nos
17 | AC DB (Rooms / Lab / Blood Bank)
| Supply & Erection of 3 Phase, 6 way, Phase seggregated 7 Seg., Double door TPN DB , with anchor fastener ,bolt & nuts and earthing. | 3 | Nos | 26890 | 4000 | 80670 | 12000
Incoming : 125A 4P MCB - 1 No
Outgoing : 40A DP RCCB (30mA) - 3 Nos
25A SP MCB - 18 Nos
18 | AC DB (MBBS Girls Hostel - Third Floor -32 rooms / 32 AC) | 2 | Nos | 26340 | 4000 | 52680 | 8000
Supply & Erection of 3 Phase, 6 way, Phase seggregated 7 Seg., Double door TPN DB , with anchor fastener ,bolt & nuts and earthing.
Incoming : 100A 4P MCB - 1 No
Outgoing : 40A DP RCCB (30mA) - 3 Nos
25A SP MCB - 18 Nos
19 | VTPN - DISTRIBUTION BOARD
| Supply & Erection of 3 Phase 8 way vertical single door the necessary angle frame, bolt & nuts incoming suitable adapter box ( cable end box ) & earthing VTPN - DB Cost should include chipping,removing debris, repacking with cement mortor, curing Complete Work. | 1 | Nos | 24320 | 4200 | 24320 | 4200
Incoming : 100A 4P MCCB 25 kA - 1 No
Outgoing : 40A TP MCB - 4 Nos
63A TP MCB - 4 Nos
20 | LIFT PANEL | 1 | Nos | 130790 | 7500 | 130790 | 7500
Supply and installation, testing and commissioning of Electrical control panel for Lift
1 No. - 125A, 36kA, FP pole MCCB with micro processor O/C,S/C, E/F releases
1 set-Indicating lamps RYB with control MCB
1 set-ON/OFF/TRIP Indicating lamp with control MCB
1 No – VAF Meter with 125 CT's
1 No - Surge Protective Devices (Type-2)
Busbars:
125A TPN Aluminum Busbar (0.7A / Sq.mm)
Outgoings:
63A FP MCCB, 16KA - 2 No
16A DP MCB - 2 NO
25 | Master Inverter DB for Emergency Lighting (14 Way SPN DB)
| Supply & Erection of single phase 14 way double door MASTER EMERGENCY LIGHTING DB lightpoint Cost should include chipping,removing debris, repacking Power plug point Cost should include chipping,removing debris, repacking with cement mortor, curing Complete Work. | 1 | NOS | 6175 | 1250 | 6175 | 1250
Incoming : 63A DP MCB - 1 No
Outgoing : 32A DP MCB - 7 Nos
II | SECTION - II (LT CABLES AND TERMINATIONS)
1 | Supply of 1100V grade LT power cables either in trench or tray or wall or as the case may be. Necessary MS clamping supports are to be provided to the following sizes of cables. (REFER SLD)
a | 3 ½ core x 300 sqmm AL.AR. cable | 1900 | mtr | 1451 | 212 | 2756900 | 402800
b | 3 ½ core x 240 sqmm AL.AR. Cable (for Girls Hostel Incoming upto Third Floor from Electrical Room) The cost should include excavation upto 1mtr of variety soil and refilling with 1 layer of river sand for 100mm, Red Brick, Caution tape, second layer of river sand for 100mm and then with removed sand to make the land look normal again | 1200 | mtr | 1180 | 166 | 1416000 | 199200
c | 3 ½ core x 185 sqmm AL.AR. Cable | RO | mtr | 955
d | 3 ½ core x 150 sqmm AL.AR. Cable | RO | mtr | 765
e | 3 ½ core x 120 sqmm AL.AR. Cable | RO | mtr | 652
f | 3 ½ core x 95 sqmm AL.AR. Cable | 200 | mtr | 501 | 112 | 100200 | 22400
g | 3 ½ core x 70 sqmm AL.AR. Cable | 200 | mtr | 398 | 99 | 79600 | 19800
h | 3 ½ core x 50 sqmm AL.AR. Cable | 600 | mtr | 297 | 87 | 178200 | 52200
i | 3 ½ core x 35 sqmm AL.AR. Cable | 200 | mtr | 220 | 69 | 44000 | 13800
j | 3 ½ core x 25 sqmm AL.AR. Cable | 400 | mtr | 184 | 53 | 73600 | 21200
k | 4 core x 16 sqmm CU. AR cable (For VRF Units) | 200 | mtr | 810 | 44 | 162000 | 8800
l | 4 core x 6 sqmm CU. AR cable (For RO Plant main cable) | R0 | Nos | 355 | 40
m | 4 core x 4 sqmm CU. AR cable | R0 | mtr | 231 | 37
n | 4 core x 2.5 sqmm CU. AR cable | 35 | mtr | 161 | 36 | 5635 | 1260
o | 3 core x 2.5 sqmm CU. AR cable (Indoor Units Power) | 300 | mtr | 127 | 36
p | 3 core x 6 sqmm CU FLEXIBLE cable | 100 | mtr | 218 | 42 | 21800 | 4200
2 | Providing necessary cable end terminations with glands & sockets to the following sizes of cables by Double compression type glands.
a | 3 ½ core x 300 sqmm AL.AR. cable | 14 | Nos | 2355 | 1200 | 32970 | 16800
b | 3 ½ core x 240 sqmm AL.AR. Cable (for Girls Hostel Incoming upto Third Floor from Electrical Room) The cost should include excavation upto 1mtr of variety soil and refilling with 1 layer of river sand for 100mm, Red Brick, Caution tape, second layer of river sand for 100mm and then with removed sand to make the land look normal again | 10 | Nos | 2185 | 1200 | 21850 | 12000
c | 3 ½ core x 185 sqmm AL.AR. Cable | RO | Nos | 1375 | 1200
d | 3 ½ core x 150 sqmm AL.AR. Cable | RO | Nos | 1375 | 1200
e | 3 ½ core x 120 sqmm AL.AR. Cable | RO | Nos | 1170 | 1200
f | 3 ½ core x 95 sqmm AL.AR. Cable | 6 | Nos | 1090 | 975 | 6540 | 5850
g | 3 ½ core x 70 sqmm AL.AR. Cable | 6 | Nos | 850 | 800 | 5100 | 4800
h | 3 ½ core x 50 sqmm AL.AR. Cable | 48 | Nos | 703 | 650
i | 3 ½ core x 35 sqmm AL.AR. Cable | 30 | Nos | 504 | 650
j | 3 ½ core x 25 sqmm AL.AR. Cable | 20 | Nos | 393 | 565 | 7860 | 11300
k | 4 core x 16 sqmm CU. AR cable (For VRF Units) | 20 | Nos | 301 | 350
l | 4 core x 6 sqmm CU. AR cable (For RO Plant main cable) | R0 | Nos | 303 | 300
m | 4 core x 4 sqmm CU. AR cable | R0 | Nos | 245 | 275
n | 4 core x 2.5 sqmm CU. AR cable | 12 | Nos | 205 | 275 | 2460 | 3300
o | 3 core x 2.5 sqmm CU. AR cable | 14 | Nos | 185 | 275 | 2590 | 3850
p | 3 core x 6 sqmm CU FLEXIBLE cable | 10 | Nos | 227 | 350
SUB TOTAL - Part – A | [5 empty] | 8365438 | 1349310
Part – B - Earthing
1 | Supplying & Erection of Earth Electrodes, Copper plate of size 600mm.x 600 mm.x 3 mm. filled with salt and charcoal mixed with sand in alternate layers 150 mm. m. from bottom. a) UPS(OT, Blood bank, Lab - wards, Emergency lighting) - 2 nos b) ELV - 1 nos c) OT Neutral - 1 nos | 4 | nos | 11875 | 4000 | 47500 | 16000
2 | Supplying & Erection of 50mm Dia Chemical Earthing Electrode 50mm Dia B Class GI pipes 3 meter filled with salt and charcoal mixed with sand in alternate layers 150 mm. m. from bottom. till 3000mm (Panels body earthing, AC Earthing) | 4 | nos | 6400 | 4000 | 25600 | 16000
3 | Charges towards Providing and Construction of Earth pit Chamber with its Cover slab suitable of 2T Load Bearing (CUSTOMER SCOPE) | 8 | nos | 6500 | 2000 | 52000 | 16000
4 | Supplying, laying and connecting 25 x 6 mm CU Flat laid in open fashion with necessary clamps, screws, interlinks etc. for tray earthing (DG Neutral) | 100 | mtr | 715 | 55 | 71500 | 5500
5 | Supplying, laying and connecting 25 x 3 mm GI Flat laid in open fashion with necessary clamps, screws, interlinks etc. for tray earthing | 200 | mtr | 71 | 55 | 14200 | 11000
6 | Supplying, laying and connecting 50 x 6 mm GI Flat laid in open fashion with necessary clamps, screws, interlinks etc. for tray earthing & DG Body earthing | 90 | mtr | 253 | 78 | 22770 | 7020
8 | Supplying, laying and connecting 2Runs of 2.5 Sq. mm. PVC Insulated copper conductor multi stranded wires in enclosed Heavy duty PVC conduits inceiling /wall / partitionsor laidin open fashion above false ceiling with necessary clamps, screws etc., | 180 | mtr | 64 | 32 | 11520 | 5760
9 | Supplying, laying and connecting 2Runs of 4 Sq. mm. PVC Insulated copper conductor multi stranded wires in enclosed Heavy duty PVC conduits inceiling /wall / partitionsor laidin open fashion above false ceiling with necessary clamps, screws etc., | 80 | mtr | 96 | 38 | 7680 | 3040
10 | Supplying, laying and connecting 2Runs of 6 Sq. mm. PVC Insulated copper conductor multi stranded wire in enclosed Heavy duty PVC conduits inceiling /wall / partitionsor laidin open fashion above false ceiling with necessary clamps, screws etc., | 20 | mtr | 149 | 48 | 2980 | 960
11 | Supplying, laying and connecting 2Runs of 10 Sq. mm. PVC Insulated copper conductor multi stranded wires in enclosed Heavy duty PVC conduits inceiling /wall / partitionsor laidin open fashion above false ceiling with necessary clamps, screws etc., | RO | mtr | 262 | 64
SUB TOTAL - Part – B | [5 empty] | 255750 | 81280
Part – C - INTERNAL ELECTRIFICATION
I | Light Fittings
1 | Supply & fixing of light fittings with their accessories screws, bolts, nuts ms ropes etc., required as per site conditions
i | 18W LED Square / Round light | 265 | Nos | 575 | 180 | 152375 | 47700
ii | 2 x 2 36W LED Clean Room fitting | 24 | Nos | 7141 | 380 | 171384 | 9120
iii | 20W Tube Light | 70 | Nos | 165 | 150 | 11550 | 10500
iv | 12W LED Square light Recess Type | RO | Nos | 540 | 280
v | 6W LED Square light (Toilets) | 20 | Nos | 276 | 200 | 5520 | 4000
vi | Up-Down light | RO | Nos | 440 | 280
vii | 240 Led Strip light with 17mm Aluminium L & Linear profile for Cove Lights based on Architect Interior Layout | RO | Mtr | 1090 | 350
viii | Driver - 80W | RO | Nos | 1350
ix | BLDC Ceiling fan <30W power Consumption | 60 | Nos | 2800 | 380 | 168000 | 22800
II | Internal Wiring (Civil Contractor Scope- However balance work scope prices needed as in case any additional works to be taken up the same shall be assessed and paid by client in line to the below BOQ)
Note:
1. Your labour cost should include chipping, removing debris, finishing of work with all necessary accessories like Bends, Junction boxes, GI flexible hose with glands and complete job required as per site condition. All the wiring should be with 2.0 mm thick PVC conduit pipe.
2. All the Points should have Phase, Neutral & Earth wire.
3. Your labour cost should include Positioning of Switch box, Light points according to the Tiles / Interiors (Civil work will be done by Client)
4. The earth wire is to be common for Each circuit and same circuit points .
5. The neutral wire should be separate for each point.
6. Each conduit should not carry more than 6 wires in ¾” conduit & 8 wires in 1” conduit.
7. All the Switch box circuit should be with 2 nos 2.5 Sq.mm & 1 no 1.0 Sq. mm wire. All the 5A Socket should be with 2 nos 1.5 Sq.mm & 1 no 1.0 Sq. mm wire to be connected from the nearest switch box circuit.
8. It must be noted that the maximum no. of points that may be considered for one circuit shall be 10 points or 1000 watts, whichever is less. The rates shall include looping between switch and light points / socket outlets and switches / exhaust fan sockets and switches / ceiling fan regulators and switches etc.,The point wiring shall be terminated in a terminal block inside the junction box. The rate shall include the cost of switches/sockets/front plates/ GI boxes, ceiling rose, holder, PVC covers etc., for complete installation. (FRLS wires) Note : Cost to exclude circuit wiring.
1 | Light Points
Supply & fixing of One way Light Point Consisting of 2R x 1.5 Sq.mm Cu. Wire & 1R x 1.5 Sq.mm Cu.Earth wire / 3C 1.5SQMM CU wire with 19/25 mm with 1.8mm thick MS Pipe, MS bend, etc., as per site condition. Supply & fixing of metal box, front plate, switches, Sheets, Screws, Slanting holder etc.,
i | 1 Light Controlled by 1 Switch | RO | Nos
ii | 2 Light Controlled by 1 Switch | RO | Nos
iii | 3 Light Controlled by 1 Switch | RO | Nos
iv | 4 Light Controlled by 1 Switch | RO | Nos
v | 3 Light Controlled by 10A SP MCB | RO | Nos
vi | 4 Light Controlled by 10A SP MCB | RO | Nos
2 | Two Way Light Points
Supply & fixing of One way Light Point Consisting of 2R x 1.5 Sq.mm Cu. Wire & 1R x 1.5 Sq.mm Cu.Earth wire with 19/25 mm with 1.8mm thick MS Pipe, MS bend, etc., as per site condition. Supply & fixing of metal box, front plate, switches, Sheets, Screws, Slanting holder etc.,
i | 1 Light Controlled by 1 Two way Switch | RO | Nos
3 | CEILING FAN
| Supply & fixing of Ceiling fan Point Consisting of 2R x 1.5 Sq.mm Cu. Wire & 1R x 1.5 Sq.mm Cu.Earth wire with 19/25 mm with 1.8mm thick MS Pipe, MS bend, etc., as per site condition. Supply & fixing of metal box, front plate, switches, Sheets, Screws, Slanting holder etc., | RO | Nos
4 | 3NOS 5 Amps plug point Controlled by Two Switch
| Supply & fixing of 5 Amps plug Point Consisting of 2R x 2.5 Sq.mm Cu. Wire & 1R x 1.5 Sq.mm Cu. Earth wire with 19/25 mm with 1.8mm thick MS Pipe, MS Bend, etc., as per site condition. Supply & fixing of Metal box, Front plate, switch, Junction boxes,Sheets, screws etc., as per the site condition. | 100 | Nos | 510 | 550 | 51000 | 55000
5 | 2 Nos 5 Amps plug point System
| Supply & fixing of 5 Amps plug Point Consisting of 2R x 2.5 Sq.mm Cu. Wire & 1R x 1.5 Sq.mm Cu. Earth wire with 19/25 mm with 1.8mm thick MS Pipe, MS Bend, etc., as per site condition. Supply & fixing of Metal box, Front plate, switch, Junction boxes,Sheets, screws etc., as per the site condition. | RO | Nos
6 | 2 Nos 5 Amps plug point TV
| Supply & fixing of 5 Amps plug Point Consisting of 2R x 2.5 Sq.mm Cu. Wire & 1R x 1.5 Sq.mm Cu. Earth wire with 19/25 mm with 1.8mm thick MS Pipe, MS Bend, etc., as per site condition. Supply & fixing of Metal box, Front plate, switch, Junction boxes,Sheets, screws etc., as per the site condition. | 50 | Nos | 310 | 550 | 15500 | 27500
7 | 5 Amps plug point on board
| Supply & fixing of 5 Amps plug Point Consisting of 2R x 2.5 Sq.mm Cu. Wire & 1R x 1.5 Sq.mm Cu. Earth wire with 19/25 mm with 1.8mm thick MS Pipe, MS Bend, etc., as per site condition. Supply & fixing of Metal box, Front plate, switch, Junction boxes,Sheets, screws etc., as per the site condition. | RO | Nos
8 | 5 Amps plug point for exhaust fan (Only for Common Wash Area)
| Supply & fixing of 5 Amps plug Point Consisting of 2R x 2.5 Sq.mm Cu. Wire & 1R x 1.5 Sq.mm Cu. Earth wire with 19/25 mm with 1.8mm thick MS Pipe, MS Bend, etc., as per site condition. Supply & fixing of Metal box, Front plate, switch, Junction boxes,Sheets, screws etc., as per the site condition. | 10 | Nos | 180 | 550 | 1800 | 5500
9 | 1 nos 16Amps Plug Points controlled by 1nos 16A Switch (Labs / Blood Bank / Cleaning power in corridor / OT)
| Supply & fixing of 16 Amps plug Point Consisting of 2R x 2.5 Sq.mm Cu. Wire & 1R x 1.5 Sq.mm Cu. Earth wire with 19/25 mm with 1.8mm thick MS Pipe, MS Bend, etc., as per site condition. Supply & fixing of Metal box, Front plate, switch, Junction boxes,Sheets, screws etc., as per the site condition. | 30 | Nos | 370 | 550 | 11100 | 16500
10 | 2Nos 16Amps Plug Points Controlled by 2 nos 16A Switch (Labs / Blood Bank )
| Supply & fixing of 2 NOS 16 Amps plug Point Consisting of 2R x 4.0 Sq.mm Cu. Wire & 1R x 1.5 Sq.mm Cu. Earth wire with 19/25 mm with 1.8mm thick MS Pipe, MS Bend, etc., as per site condition. Supply & fixing of Metal box, Front plate, switch, Junction boxes,Sheets, screws etc., as per the site condition. | 40 | Nos | 740 | 550 | 29600 | 22000
11 | Data Point
| Supply & fixing of Computer Point Modular plate type RJ-45 jack, Both ends ferrules and Termination metal box, junction box, front plate & Screws , etc.,Complete Work. | 85 | Nos | 290 | 125 | 24650 | 10625
12 | Telephone Point
| Supply & fixing of Telephone Point Modular plate type RJ-11 jack, Both ends ferrules and Termination metal box, junction box, front plate & Screws , etc.,Complete Work. | 85 | Nos | 280 | 125 | 23800 | 10625
13 | Television Point
| Supply & fixing of Television Point Modular plate type RJ-6 jack, Both ends ferrules and Termination metal box, junction box, front plate & Screws , etc.,Complete Work. | 20 | Nos | 490 | 125 | 9800 | 2500
NURSE CALLING SYSTEM
14 | Nurse Call Point
15 | Supply & fixing of Nurse Call Point Modular plate , Both ends ferrules and Termination metal box, junction box, front plate & Screws , etc.,Complete Work.
| Head Panel Unit with Patient Handle (Flexible wired) | 50 | Nos | 5550 | 800 | 277500 | 40000
| Washroom Unit with Flexible Wire and Water proof | 24 | Nos | 3400 | 450 | 81600 | 10800
16 | ELITE Model (IP based): (IP Room Nursing Station) a. NURSE CALL PROCESSOR SOC Processor to collect information from all the connected Rooms, send indicator information to Rooms, show the room call status on LCD TV & b. 27” LCD MONITOR is used for both Audio announcement and Visual Display in Multi-color | 2 | Nos | 28500 | 3000 | 57000 | 6000
17 | N.S.EXTENDER (8 Port) | 2 | Nos | 11100 | 2000 | 22200 | 4000
18 | DOOR / BED INDICATOR - Wall mountable type, ABS plastic enclosure, Semi-circular shaped Indicator with Tri-color Indication | 50 | Nos | 1410 | 375 | 70500 | 18750
19 | Supply and Laying of Data Cabling in (HMS) PVC fire retardant conduit in exposed places and above false ceiling complete with terminations and accessories.
a) | 4 pair CAT-6 cable | 850 | Mtrs | 55 | 28 | 46750 | 23800
20 | METAL ENCLOSURE
Supply & fixing of metal enclosure with breakers.
i | 4 Pole Metal Enclosure | 16 | Nos | 420 |  | 6720 | 0
ii | 25A DP MCB | 16 | Nos | 485 |  | 7760 | 0
iii | 16A SP MCB | 16 | Nos | 172 |  | 2752 | 0
21 | Modular Back Box & Front Plate
Supply & Fixing of the back box & modular plate with their accessories as per site conditions.
i | 2M Back Box & Front Plate | RO | Nos
ii | 3M Back Box & Front Plate | 100 | Nos | 122 | 27 | 12200 | 2700
iii | 4M Back Box & Front Plate | RO | Nos
iv | 6M Back Box & Front Plate | 40 | Nos | 158 | 40 | 6320 | 1600
v | 8M Back Box & Front Plate | 120 | Nos | 195 | 55 | 23400 | 6600
vi | 12M Back Box & Front Plate | RO | Nos
vii | 18M Back Box & Front Plate | RO | Nos
22 | Lighting Circuit
| Supply & laying of Lighting Circuit -2R x 2.5sqmm Cu. Wire & 1R x 1.5 Sq.mm Cu.Earth Wire with 19/25mm with 1.8mm thick MS Pipe,Bend, etc., Supply and fixing of termination, with sockets and Screws, etc., as per the site condition. | 6450 | Mtrs | 91 | 36 | 586950 | 232200
23 | Light Point Circuit
| Supply & laying of Lighting Circuit -2nos x 1.5sqmm Cu. Wire &1No x 1.5 Sq.mm Cu.Earth Wire with 19/25mm with 1.8mm thick MS Pipe,Bend, etc.,. Supply and fixing of termination, with sockets and Screws, etc., as per the site condition. | RO | Mtrs | 72 | 32
24 | Power Circuit
| Supply & laying of Lighting Circuit -2R x 2.5sqmm Cu. Wire & 1R x 1.5 Sq.mm Cu.Earth Wire with 19/25mm with 1.8mm thick MS Pipe,Bend, etc., Supply and fixing of termination, with sockets and Screws, etc., as per the site condition. | 1600 | Mtrs | 91 | 36 | 145600 | 57600
25 | Power Circuit
| Supply & laying of Power Circuit -2R x 4.0 sqmm Cu. Wire & 1R x 1.5 Sq.mm Cu.Earth Wire with 19/25mm MS Pipe, Bend etc., Supply and fixing of termination, with sockets and Screws, etc., as per the site condition. | 1100 | Mtrs | 122 | 39 | 134200 | 42900
26 | Power Circuit (Equipment requirement)
| Supply & laying of Power Circuit - 4C 6.0 sqmm Flexible Cu. Wire with clamps, screws etc.,as per site condition. Supply and fixing of termination, with sockets and Screws, etc., as per the site condition. | 200 | Mtrs | 338 | 44 | 67600 | 8800
27 | MS CONDUIT & MS JUNCTION BOX (ABOVE FALSE CEILING)
a | Supply & fixing of 25MM MS conduit (HEAVY) with their screws, fixers etc., as per site conditions. | 3000 | Mtrs | 86 | 36 | 258000 | 108000
b | Supply & fixing of MS junction box with their screws, fixers etc., as per site conditions.
i | 4WAY MS JN. BOX | 400 | Nos | 31 | 5 | 12400 | 2000
ii | 3WAY MS JN. BOX | 300 | Nos | 31 | 5 | 9300 | 1500
iii | 2WAY MS JN. BOX | 320 | Nos | 31 | 5 | 9920 | 1600
iv | 2WAY 90DEG MS JN. BOX | 300 | Nos | 31 | 5 | 9300 | 1500
v | 1WAY MS JN. BOX | 210 | Nos | 31 | 5 | 6510 | 1050
vi | MS BEND | 400 | Nos | 31 | 5 | 12400 | 2000
28 | PVC CONDUIT & PVC JUNCTION BOX ( WALL CONCEALED)
I | Supply & fixing of 25MM PVC conduit (HEAVY) with their screws, fixers etc., as per site conditions. | 750 | Mtrs | 41 | 21 | 30750 | 15750
II | Supply & fixing of PVC junction box with their screws, fixers etc., as per site conditions.
i | 4WAY PVC JN. BOX | RO | Nos | 18 | 5
ii | 3WAY PVC JN. BOX | RO | Nos | 18 | 5
iii | 2WAY PVC JN. BOX | RO | Nos | 18 | 5
iv | 2WAY 90DEG PVC JN. BOX | RO | Nos | 18 | 5
v | 1WAY PVC JN. BOX | RO | Nos | 18 | 5
vi | PVC BEND | RO | Nos | 18 | 5
29 | Supply & Fixing of MS Wall Junction Box |  | Nos
| a) 4" x 4 " x 3" MS Wall Junction Box | 60 | Nos | 54 | 35 | 3240 | 2100
| b) 6" x 4 " x 3" MS Wall Junction Box | 30 | Nos | 68 | 35 | 2040 | 1050
| b) 8" x 6 " x 3" MS Wall Junction Box | 20 | Nos | 115 | 45 | 2300 | 900
30 | CABLE TRAYS
G I Perforated Type Cable Trays / WIRE TRAY :
Supply , Erecting & connecting the following 2.0 mm Thickness G I Perforated Type Cable Trays with joining plates, stiffners, facility for clamping cables / conduits at every 450mm intervals, suitable bracket supports for ceiling suspension (or) suitable bracket supports for wall suspension,etc., All as per site condition shall be fabricated / erected and as per Employer / Consultant and nuts and any other associated elbows, bends, bolts and nuts and any other associated accessories to complete the job.
i | Supply & Fixing of Ms Support C Slotted angles with including fixtures like Base plates, Anchor Fastner, Scwres, Bolts, Nuts, Washer etc., required as per site Conditions. | 1 | Tons | 72000 | 40000 | 72000 | 40000
ii | 600 mm width x 100mm Height | 90 | Mtrs | 1035 | 410 | 93150 | 36900
iii | 450 mm width x 100mm Height | 50 | Mtrs | 845 | 345 | 42250 | 17250
iii | 300 mm width x 100mm Height | 120 | Mtrs | 646 | 280 | 77520 | 33600
iii | 150 mm width x 100mm Height | 200 | Mtrs | 455 | 190 | 91000 | 38000
31 | Retrofit and Rework in MBBS Girsl Hostel Building
MBBS girls hostel third floor new building incoming power supply provision Rework and alteration in existing panel Provision of power supply for terrace RO plant 3 phase FP 32 A MCB metal clad box installation and earthing cable laying from GF to Third floor DB's and terrace RO system
SUB TOTAL - Part – C | [5 empty] | 2957211 | 1003320
Part – D ( POWER BACKUP SYSTEM)
SECTION I - Inverter for Emergency Lighting
1 | 1.15 KVA Inverter (Online UPS)
| 15KVA Pure Sine Wave UPS / Inverter with 2 hours battery backup, Input: 3 Phase 415V AC (Voltage range: 340V AC to 440V AC), 50HZ, Transfer Time not more than 10ms with Lead Acid battery - 100AH, Efficiency >80% suitable for 2 hours backup | 1 | Set | 332640 | 2800 | 332640 | 2800
SECTION II - UPS
1 | 30 KVA Online UPS with Isolation Transformer For OT
| Supply, Installation, testing and commissioning 30 KVA 3 phase input (415 V +/- 15%), 3 phase output (415 V + 1%) on line UPS + innbuilt isolation transformer with 60 minutes battery backup each complete with battery rack. | 1 | Set | 790314 | 5500 | 790314 | 5500
2 | 20 KVA Online UPS with isolation transformer Medical Equipments (Lab)
| Supply, Installation, testing and commissioning 20 KVA 3 phase input (415 V +/- 15%), 3 phase output (415 V + 1%) on line UPS + innbuilt isolation transformer with 60 minutes battery backup each complete with battery rack. | 1 | Set | 535000 | 4900 | 535000 | 4900
3 | Removal Refixing of 20 KVA Online UPS in Blood Bank
| Removal and Refixing of 20 KVA 3 phase input (415 V +/- 15%), 3 phase output (415 V + 1%) on line UPS + innbuilt isolation transformer with existing batter from Old Blood Bank to New Blood Bank location including all accessories, interconnecting cable, battery stand, etc., | 1 | Set |  | 12500 | 0 | 12500
4 | 10 KVA Online UPS For Rooms
| Supply, Installation, testing and commissioning 10 KVA 3 phase input (415 V +/- 15%), 1 phase output (230 V + 1%) on line UPS with 60 minutes battery backup each complete with battery rack. | 1 | Set | 248650 | 2800 | 248650 | 2800
5 | 1.5 KVA Online inverter with Inbuilt Lithium Ferro Phosphate for Girls Hostel Third Floor
| Supply, Installation, testing and commissioning 1kW 1 phase input (230 V +/- 10%), 1 phase output (230 V + 1%) on line Inverter with 180 minutes battery backup each complete with builtin Lithium Ferro Phosphate battery | 1 | Set | 176960 | 2200 | 176960 | 2200
SECTION IV - MS Supports
A | Ms Supports Angles (Light Fixing, Cable Tray fixing in power room for Bridge & inside the building)
1 | Supply & Fixing of Ms Support 50 x 50 angle with including fixtures like Base plates, Anchor Fastner, Scwres, Bolts, Nuts, Washer etc., required as per site Conditions. | 4 | Tons | 72000 | 40000 | 288000 | 160000
2 | MS Checker plate with necessary sizes to be provided in Exisiting EB room near HT yard and DG Area | 1.5 | Tons | 81000 | 40000 | 121500 | 60000
SUB TOTAL - Part – D | [5 empty] | 2371564 | 190700
*Note: The Above scope is prepared based on standard design parameters, however in case of any addition of Points, Lights, Circuits required based on client shall be approved as per unit rate finalized as above

## FAS
Sl.No | DESCRIPTION
|  | Qty | Unit | Rate |  | Amount |  | Billing Details
|  |  |  | Supply | Erection | Supply | Erection | Invoice Number
1 | Supply, installation, testing and commissioning of ADDRESSABLE Multicriteria DETECTOR(above with RI based on site condition it can be used) (Existing make Ravel to be used) | 165 | Nos | 1900 | 350 | 313500 | 57750 | APCS/G/210/23-24 APCS/G/211/23-24 APCS/G/212/23-24 APCS/G/213/23-24 APCS/G/214/23-24 APCS/G/232/23-24 - Ere
2 | Supply, installation, testing and commissioning of ADDRESSABLE MANUAL PULL STATION (Existing make Ravel to be used) | 4 | Nos | 2500 | 350 | 10000 | 1400 | APCS/G/175/23-24 APCS/G/232/23-24 - Ere
3 | Supply, installation, testing and commissioning of HOOTER WITH STROBE LIGHT (Existing make Ravel to be used) | 4 | Nos | 1550 | 350 | 6200 | 1400 | APCS/G/209/23-24 APCS/G/232/23-24 - Ere
4 | Supply, installation, testing and commissioning of ADDRESSABLE MONITOR MODULE (Existing make Ravel to be used) | 4 | Nos | 2500 | 350 | 10000 | 1400 | APCS/G/209/23-24 APCS/G/232/23-24 - Ere
5 | Supply, installation, testing and commissioning of ADDRESSABLE FAULT ISOLATOR MODULE (Existing make Ravel to be used) | 4 | Nos | 2500 | 350 | 10000 | 1400 | APCS/G/209/23-24 APCS/G/232/23-24 - Ere
6 | Supply, installation, testing and commissioning of ADDRESSABLE Relay MODULE (Existing make Ravel to be used) | 4 | Nos | 2240 | 2200 | 8960 | 8800 | APCS/G/209/23-24 APCS/G/232/23-24 - Ere
7 | Supply, installation, testing and commissioning of ADDRESSABLE FIRE ALARM CONTROL PANEL with one loop card (Existing make Ravel to be used) | 1 | Nos | 52500 | 2200 | 52500 | 2200 | APCS/G/210/23-24 APCS/G/232/23-24 - Ere
8 | Supply, laying, testing and commissioning of 2Core, 1.5Sqmm FRLS Cu FLEXIBLE Cable | 320 | Mtrs | 58 | 22 | 18560 | 7040 | APCS/G/065/23-24 APCS/G/214/23-23 APCS/G/133/23-24 - Ere APCS/G/232/23-24 - Ere
9 | Fire Exit Boards Illuminated, Exit Route Map as required at site | 1 | Lot |  | 20000 | 0 | 20000
10 | Design, Testing & Commissioning Charges | 1 | Lot |  | 65000 | 0 | 65000
SUB TOTAL | [5 empty] | 429720 | 166390
*Note: The Above scope is prepared based on standard design parameters, however in case of any addition of detectors and mcp's required based on compliance shall be approved as per unit rate finalized as above

## CCTV & Networking
Architect
MEP Consultant
Contractor
TITLE :
Sl.No | DESCRIPTION | Qty | Unit | Rate |  | Amount |  | Billing Details
|  |  |  | Supply | Erection | Supply | Erection | Invoice Number | Date
CCTV BOQ
1 | IP camera-2MP, fixed lens, IR upto 20 meters-Bullet | 8 | Nos | 2550 | 280 | 20400 | 2240 | APCS/G/128/23-24 APCS/G/133/23-24 - Ere APCS/G/175/23-24 APCS/G/232/23-24 - Ere | 03.08.2023 08.09.2023 13.10.2023
2 | IP camera-2MP, fixed lens, IR upto 20 meters-Dome | 18 | Nos | 2450 | 280 | 44100 | 5040 | APCS/G/127/23-24 APCS/G/133/23-24 - Ere APCS/G/175/23-24 APCS/G/232/23-24 - Ere | 03.08.2023 08.09.2023 13.10.2023
3 | NVR 32 channel | 1 | Nos | 34500 | 2200 | 34500 | 2200 | APCS/G/175/23-24 APCS/G/232/23-24 - Ere | 08.09.2023 13.10.2023
4 | WD HDD Sata 8TB for 30 days storage | 2 | Nos | 9500 | 500 | 19000 | 1000 | APCS/G/175/23-24 APCS/G/232/23-24 - Ere | 08.09.2023 13.10.2023
5 | 16 port POE switch | 3 | Nos | 9500 | 550 | 28500 | 1650 | APCS/G/175/23-24 APCS/G/232/23-24 - Ere | 08.09.2023 13.10.2023
6 | CAT 6 cable and accessories (includes nurse calling) | 1200 | Mtrs | 55 | 24 | 66000 | 28800 | APCS/G/072/23-24 APCS/G/129/23-24 APCS/G/165/23-24 APCS/G/215/23-24 APCS/G/231/23-24 APCS/G/133/23-24 - Ere APCS/G/323/23-24 - Ere APCS/BS/503A/23-24 | 14.06.2023 03.08.2023 30.08.2023 03.10.2023 13.10.2023
8 | 6U rack and accessories | 2 | Nos | 5800 | 1750 | 11600 | 3500 | APCS/G/175/23-24 APCS/G/232/23-24 - Ere | 08.09.2023 13.10.2023
9 | 17U rack and accessories | 1 | Nos | 22500 | 2750 | 22500 | 2750 | APCS/G/175/23-24 APCS/G/232/23-24 - Ere | 08.09.2023 13.10.2023
10 | 65 inch Led display for CCTV 24x7 operation | RO | Nos | 54000 | 1750
11 | HDMI cable 30 mtrs | RO | Nos | 7500 | 550
12 | Design, Testing & Commissioning Charges | 1 | Lot |  | 22000 | 0 | 22000
NETWORKING BOQ
1 | 8 port POE switch | 2 | Nos | 5800 | 325 | 11600 | 650 | APCS/G/335/23-24 | 11.12.2023
2 | WIFI AP - Dualband Wi-Fi 6 (coverage 4000Sq Ft) | 7 | Nos | 29500 | 550 | 206500 | 3850 | APCS/G/335/23-24 | 11.12.2023
3 | CAT 6 cable and accessories | 350 | Mtrs | 55 | 24 | 19250 | 8400 | APCS/G/215/23-24 APCS/G/232/23-24 - Ere | 03.10.2023 13.10.2023
4 | Supply & Laying testing and Commissioning of 100 Pair 0.5mm Dia tinned copper conductor of telephone cable with 20 / 25 mm Dia 1.8mm Pvc pipe , | 85 | Mtrs | 138 | 24 | 11730 | 2040 | APCS/G/336/23-24 | 11.12.2023
5 | Supply & fixing the 50 pair krone connector with suitable enclosure with locking arrangement Telephone Tag blocks housed in MS Boxes (with hinged cover and duly painted) recessed in wall with adequate knockouts including chase cutting and making the surface good and making connections complete as required | 1 | Nos | 4500 | 1250 | 4500 | 1250 | APCS/G/335/23-24 | 11.12.2023
6 | CAT 6 cable and accessories for Analogue Phone | 600 | Mtrs | 55 | 24 | 33000 | 14400
7 | Cat 6 Cable Terminations For Network | 50 | Sets | 220 | 180 | 11000 | 9000
8 | Supplying & laying of Coaxial type Television cable of RG - 6 Wire with 20 / 25 mm Dia 1.8mm Pvc pipe , | 450 | Mtrs | 42 | 24 | 18900 | 10800 | APCS/G/129/23-24 APCS/G/128/23-24 APCS/G/133/23-24 - Ere | 03.08.2023
9 | SITC of RG 11 Co -axial unarmored cable for Analogue Phone in each room | RO | Mtrs
10 | Fixing of 4 Way TV TAP OFF | RO | Nos
11 | Fixing of 4 Way TV Spliter | RO | Nos
12 | 100 pair cable (from tele. Tag block to EPABX) | RO | Mtrs
13 | Krone box suitable for above | RO | nos
13 | Design, Testing & Commissioning Charges | 1 | Lot |  | 18000 | 0 | 18000
SUB TOTAL | [5 empty] | 563080 | 137570
*Note: The Above scope is prepared based on standard design parameters, however in case of any addition of camera required based on compliance shall be approved as per unit rate finalized as above